 ANNEX B – Energy Audit Report For Building Cooling System









Date: DD/MM/YEAR

ENERGY AUDIT REPORT FOR BUILIDNG COOLING SYSTEM
FOR 

ENTER BUILDING NAME








Submitted By








Enter name of PE/Energy Auditor










PE (Mech) Registration No*: Enter No.










Energy Auditor Registration No*: Enter No.


*Delete whichever is not applicable

Contents


211.0
Building Information


212.0
Energy Audit Information For Building Cooling System


222.1
Chilled Water Plant information*


232.2
Chilled Water Plant Normal Operating Hours


233.0
Instrumentations


244.0
Chiller Plant Performance Analysis


264.1
Summary of Chilled Water Plant Performance


265.0
Summary of Heat Balance




22Table 1: Chiller Information (Example)


22Table 2: Ancillary equipment Information (Example)


23Table 3: Instrumentation Table (Example)


27Table 4: Heat Balance Summary




 TOC \h \z \c "Figure" 
24Figure 1: Super-imposed plot of daily Cooling Load Profile (Example)


24Figure 2: Histogram of Cooling Load Occurrences (Example)


25Figure 3:Super-imposed plot of daily chiller plant efficiency (Example)


25Figure 4: Scatter plot of chiller plant efficiency over cooling load (Example)


26Figure 5: System Level Heat Balance Plot (Example)





1.0
Building Information

Enter a brief description of the building here. 

Project Reference Number
: Enter project reference indicated in CORENET submission
Building Name


: 

Building Address

:

Postal Code


:

Building Type


:

Building Age


:

Date of last Energy Audit Submission
:

Gross floor area (GFA), m2
: 

Air conditioned area, m2
:

2.0
Energy Audit Information For Building Cooling System
Enter PE(Mech)(Mechanical)/ Energy Auditor Name was appointed by Enter Owner Name/ MCST, owner of Enter Building Name to be the Energy Auditor for the 3 yearly submission of the operating system efficiency (OSE) of the centralized Chilled Water Plant. The report will present the performance of centralized Chilled Water Plant efficiency based on the measurements from the permanent instrumentations installed on site.

Location 


:
 Enter location of Chilled Water Plant 

Energy Audit Period

: 
Enter  Energy Audit period *Note: Minimum 1 
week
Date of notice served

:
Enter date of notice served by BCA

Date of submission in notice
: 
Enter submission deadline stipulated in BCA notice 

Data Logging Interval

:
1 minute sampling

Trend Logged Parameters*
:
Chilled Water Supply main header temperature 
Chilled Water Return main header temperature 

Chilled Water flow rate at chilled water return main header 

Condenser Water Supply main header temperature 

Condenser Water Return main header temperature 

Condenser water flow rate at condenser water return main header 

Power input to Chiller(s)

Power input to Chilled water pump(s)

Power input to Condenser water pump(s)

Power input to Cooling tower(s)

* Trend logged parameters are not limited to the above and may vary depending on the piping and electrical circuit design.

2.1
Chilled Water Plant information* 
Table 1: Chiller Information (Example)

	ID
	Description
	Type 
	Name plate motor (kW)
	Cooling Capacity (RT) 
	Chilled water LWT
	Chilled water  ∆T
	Rated Efficiency

kW/RT
	Year Installed

	CH01
	Chiller 1
	Centrifugal
	150
	1000
	6.7 °C
	5.5°C
	0.55
	2012

	CH02
	Chiller 2
	VSD Screw
	90
	500
	6.7 °C
	5.5°C
	0.52
	2012


	ID
	Description
	Name plate motor (kW)
	Pump Head

(m)
	Flow rate  (L/S)
	Rated Pump/ Fan efficiency  
	Rated Motor Efficiency

	CHWP01
	Chilled water pump 1
	55 
	30 
	151.2
	85%
	95%

	CHWP02
	Chilled water pump 2
	30 
	30 
	75.6
	85%
	95%

	CWP01
	Condenser water pump 1
	45 
	20 
	189
	85%
	95%

	CWP02
	Condenser water pump 2
	22 
	20 
	94.5
	85%
	95%

	CT01
	Cooling tower 1
	45 
	-
	130
	75%
	92%

	CT02
	Cooling tower 2
	45 
	-
	130
	75%
	92%


Table 2: Ancillary equipment Information (Example)

*Based on equipment design specifications and name plate ratings. 

2.2
Chilled Water Plant Normal Operating Hours
Monday to Friday

: 
0730 – 1900 Hrs 

Saturday


: 
No operations
Sunday



: 
No operations

Note: The operating hours should follow the table in clause 6.1.4 
3.0
Instrumentations
Accurate measuring instruments complying with the Code on Environmental Sustainability Measures for Existing Buildings or the Code for Environmental Sustainability of Buildings (2nd edition and onwards) that is prevailing at the time of installation were used during the audit to gather information on the power consumption, temperatures and flow rate.

The points of measurements are listed in the following table:

	ID
	Description
	Sensor Type
	Installation Location
	Measurement/

Calibration range
	Measurement Uncertainty
(%)  
	Last Calibration Date 

	TT01
	CHWS Temperature
	10K Ω Thermistor
	CHWS Header
	0°C - 40°C
	±0.03    °C
	15/10/2012

	TT02
	CHWR Temperature
	10K Ω Thermistor
	CHWR Header
	0°C - 40°C
	±0.03    °C
	15/10/2012

	TT03
	CWS Temperature
	10K Ω Thermistor
	CWS Header
	0°C - 40°C
	±0.03    °C
	15/10/2012

	TT04
	CWR Temperature
	10K Ω Thermistor
	CWR Header
	0°C - 40°C
	±0.03     °C
	15/10/2012

	FM01
	CHW Flow


	Magnetic Full Bore
	CHWR Header
	30 l/s- 200 l/s
	0.5%
	20/10/2012

	FM02
	CW Flow
	Magnetic Full Bore
	CWR Header
	30 l/s- 200 l/s
	0.5%
	20/10/2012

	kW01
	Chiller 1 Power


	True RMS, 3 phase
	ACMSB1
	60 – 600 kW
	0.5% 
	30/10/2012

	kW02
	Chiller 2 Power


	True RMS, 3 phase
	ACMSB2
	60 – 600 kW
	0.5%
	30/10/2012

	kW03
	CHW Pump 1 & 2 Power
	True RMS, 3 phase
	
	20 – 200 kW
	0.5%
	30/10/2012

	kW04
	CW Pump 1 & 2 Power
	True RMS, 3 phase
	CHW SB
	20 – 200 kW
	0.5%
	30/10/2012

	kW05
	CT 1 & 2 Power
	True RMS, 3 phase
	CT Panel
	15 – 150 kW
	0.5%
	30/10/2012


Table 3: Instrumentation Table (Example)

4.0
Chiller Plant Performance Analysis
[image: image1.png]dd/mm/year -

dd/mm/year

Daily Cooling Load Profile

Mon
Tue

——Wed

=Thu

———Fri

00:00:€C
00:00:7C
00:00:TC
00:00:0C
00:00:6T
00:00:8T
00:00:LT
00:00:9T
00:00:5T
00:00:vT
00:00:€T
00:00:CT
00:00:TT

00:00:0T

00:00:6
00:00:8
00:00:£
00:00:9
00:00:9

2500

2000 -

1500
1000

suoyy

500

Time (hh:mm:ss)





Figure 1: Super-imposed plot of daily Cooling Load Profile (Example)

[image: image2.png]Occurences

3500

3000

2500

2000

1500

1000

500

Frequency of Cooling Load Occurences:

dd/mm/year- dd/mm/year

1000 1600 2200
Rtons

>2200





Figure 2: Histogram of Cooling Load Occurrences (Example)

[image: image3.png]dd/mm/year -

dd/mm/year

Chiller Plant Efficiency Profile

Mon
——Tue
——Wed

Thu

———Fri

00:00:€C
00:00:7C
00:00:TC
00:00:0C
00:00:6T
00:00:8T
00:00:LT
00:00:9T
00:00:5T
00:00:vT
00:00:€T
00:00:CT
00:00:TT
00:00:0T ;
00:00:6

00:00:8

0.9
0.8
0.7
0.6
0.5

0.4
03
0.2
0.1

La/mx

Time (hh:mm:ss)





Figure 3:Super-imposed plot of daily chiller plant efficiency (Example)
[image: image4.png]Chiller Plant Efficiency VS Cooling Load:
dd/mm/year- dd/mm/year

204 ope, ooy
03
0.2
0.1

0 200 400 600 800 1000 1200 1400 1600 1800 2000 2200 2400 2600
Rtons





Figure 4: Scatter plot of chiller plant efficiency over cooling load (Example)
4.1
Summary of Chilled Water Plant Performance

	
	Efficiency
	Unit

	
	Daytime^
	Night-time~
	

	Chiller(s) efficiency
	
	
	kW/RT

	Chilled water pump(s) efficiency
	
	
	kW/RT

	Condenser water pump(s) efficiency*
	
	
	kW/RT

	Cooling tower(s) efficiency*
	
	
	kW/RT

	Overall chiller plant efficiency
	
	
	kW/RT


*Not applicable to air-cooled Chilled Water Plant
~For hotels and other developments with 24-hour operations only; Night-time shall refer to the period from 11pm – 7am; 

^ For hotels and other developments with 24-hour operations, day-time shall refer to the period from 7am – 11pm; for all other developments, daytime shall refer to the normal operating hours stipulated in clause 6.1.4

5.0
Summary of Heat Balance

[image: image5.png]Heat Balance Percentage: dd/mm/year -
dd/mm/year

30%

25%

20%

15% 1

10%
5%
0%

59

-10%
-15%

-20%

-25%

-30%





Figure 5: System Level Heat Balance Plot (Example)
	
	Quantity
	Unit
	Formula

	Sum of total electrical energy used
	
	kWh
	(A)

	Sum of total cooling produced
	
	RTh
	(B)

	Sum of total heat rejected
	
	RTh
	(C)

	Chiller Plant Efficiency
	
	kW/RT
	(A) /  (B)

	Total Heat Balance Data Count
	
	-
	(D)

	Data Count > + 5% error
	
	-
	(E)

	Data Count < - 5% error
	
	-
	(F)

	Data Count within ±5% error
	
	-
	(G) = (D) – (E) – (F)

	% Heat Balance within ±5% error
	
	%
	100 x (G) / (D) 


Table 4: Heat Balance Summary

0.79%





32.19% %





8.54 %





14.35 %





42.85 %





1.28 %





± 5%








1 | Page

