[image: image1.png]e) Unitywater

Serving you today, investing in tomorrow.





F8943 - SPS Commissioning Check Sheet Template

Document No: F8943

Revision No: 6

Last Review Date: 28/01/2021

[image: image2.jpg]e

Se

o) Unitywater

Serving you today, investing in tomorrow.




Next Review Date: 28/01/2023

F8943 - SPS Commissioning Check Sheet Template


Document Details

This document is only valid on the day it was printed.

	Document Owner
	Manager Capital Delivery

	
	

	References
	SPS Commissioning Worksheet

	
	End to End Test Sheet

	
	


	This document may not, in whole or part, be copied, photocopied, reproduced or translated without
	P a g e
	ii

	prior consent from the CEO, Unitywater.
	
	

	
	
	


Printed copies are uncontrolled.

Document No: F8943

Revision No: 6

Last Review Date: 28/01/2021


Next Review Date: 28/01/2023

F8943 - SPS Commissioning Check Sheet

Template


Contents

Contents
3
General
4
Vendor Verification
5
General
5
Mechanical
5
Civil
5
Factory Acceptance Testing (FAT)
6
Electrical, Instruments and Control (E, I & C)
6
Pre-commissioning
7
Preliminaries Checklist
7
Pre-commissioning Checklist
9
General
9
Network
9
Electrical, Instruments and Control (E, I & C)
9
Mechanical
13
Wet Testing
15
Commissioning Schedule
15
General
15
Wet Well Level Sensor Checks
15
Pump Checks
15
Pump Control Checks
16
Generator Checks
18
Wet Testing Signoff
18
SAT / Performance Testing
19
SAT Schedule
19
SAT Pre-start Checks
19
Wet Well Level Sensor Checks
19
Pump Checks
19
Pump Control Checks
19
Generator Checks
21
SAT Signoff
22
	This document may not, in whole or part, be copied, photocopied, reproduced or translated without
	P a g e
	3

	prior consent from the CEO, Unitywater.
	
	

	
	
	


Printed copies are uncontrolled.

Document No: F8943

Revision No: 6

Last Review Date: 28/01/2021


Next Review Date: 28/01/2023

F8943 - SPS Commissioning Check Sheet Template


General

In using this document, due consideration of all other relevant Unitywater Standard Drawings and Unitywater Standard Specifications should be adhered to.

	This document may not, in whole or part, be copied, photocopied, reproduced or translated without
	P a g e
	4

	prior consent from the CEO, Unitywater.
	
	

	
	
	


Printed copies are uncontrolled.

Document No: F8943

Revision No: 6

Last Review Date: 28/01/2021


Next Review Date: 28/01/2023

F8943 - SPS Commissioning Check Sheet Template


Vendor Verification

	PROJECT TITLE:
	
	FINANCE NO:

	
	
	
	

	General
	
	Result / Init. / Date

	
	
	
	

	Mechanical
	
	

	
	
	
	
	

	1.
	Pump test results been reviewed and conform with applicable standards
	OK

	2.
	Flowmeter Calibration certificate received
	
	OK

	Civil
	
	
	
	

	
	
	
	
	

	3.
	Check pressure test on rising main has passed
	
	OK

	4.
	Check wet-well leakage test (hydrotest) has passed
	
	OK

	
	
	
	

	CONSTRUCTOR
	
	

	
	
	
	
	

	Name:
	
	Position:
	Signature:
	Date:

	
	
	
	

	UNITYWATER SIGNOFF
	
	

	
	
	
	
	

	Name:
	
	Position:
	Signature:
	Date:

	
	
	
	
	


	This document may not, in whole or part, be copied, photocopied, reproduced or translated without
	P a g e
	5

	prior consent from the CEO, Unitywater.
	
	

	
	
	


Printed copies are uncontrolled.

Document No: F8943

Revision No: 6

Last Review Date: 28/01/2021


Next Review Date: 28/01/2023

F8943 - SPS Commissioning Check Sheet Template


PROJECT TITLE:

Factory Acceptance Testing (FAT)

Electrical, Instruments and Control (E, I & C)

Switchboards





FINANCE NO:

Result / Init. / Date


1. The switchboard manufacturer has been provided with current Unitywater Standard Switchboard Drawings (OR, if “Design and Construct”, the ‘For Construction’ drawings have been reviewed by Unitywater and provided to the switchboard manufacturer)





OK


2. The switchboard manufacturer has undertaken a full point-to-point test on all switchboard wiring





OK


3. The switchboard manufacturer has provided evidence of point-to-point testing in the form of marked up wiring drawings (each connection highlighted as tested)





OK

4. Any changes, outcomes or additional detail resulting from FAT testing have been marked on the drawings with the highlighted test connections. Mark-ups include all available circuits, inputs, power supply voltages, labels, wire numbers, terminals etc. These marked-up drawings are labled ‘FAT’.





OK

	5.
	Cabinet and paintwork have been inspected for any visual damage
	OK

	6.
	The following is as per current drawings:
	OK

	
	•
	Incomer arrangements
	

	
	•
	Cable entry provisions
	

	
	•
	Interlocking provisions
	

	
	•   Incomer protection (Fault current rating) and discrimination
	

	7.
	Switchboard rating nameplate is attached
	OK

	8.
	Switchboard Test Certificate has been checked
	OK

	9.
	Software used during FAT is available
	OK

	10.
	Any deficiencies have been recorded to a ‘FAT punchlist register’ and rectified
	OK

	
	
	
	


Instrumentation


11. Calibration certificates have been received for instruments





OK

	
	Software
	
	

	
	
	
	
	
	

	
	12.
	Software for Outstation Type is loaded
	
	OK

	
	13.
	Software blocks have been fat tested (if non standard)
	OK

	
	
	
	
	

	
	CONSTRUCTOR
	
	

	
	
	
	
	
	

	
	Name:
	
	Position:
	Signature:
	Date:

	
	
	
	
	

	
	UNITYWATER SIGNOFF
	
	

	
	
	
	
	
	

	
	Name:
	
	Position:
	Signature:
	Date:

	
	
	
	
	
	


	This document may not, in whole or part, be copied, photocopied, reproduced or translated without
	P a g e
	6

	prior consent from the CEO, Unitywater.
	
	

	
	
	


Printed copies are uncontrolled.

Document No: F8943

Revision No: 6

Last Review Date: 28/01/2021


Next Review Date: 28/01/2023

F8943 - SPS Commissioning Check Sheet Template


Pre-commissioning


	PROJECT TITLE:
	FINANCE NO:


	
	Preliminaries Checklist
	Result / Init. / Date

	
	
	
	

	1.
	Check all commissioning personnel have been inducted to site
	OK

	
	
	
	

	2.
	Check risk assessments and SWMS have been produced for all Pre-
	OK

	
	
	commissioning and Commissioning activities
	

	
	
	
	



3. The site is safe for commisisoning works to commence. Safety requirements include:

· Covers and grills installed and flush

· Davit mounting points certified

· Fall arest mounting points certified

· Handrails, fencing, gates and chains installed correctly

· Emergency procedures available

· Safety signage in place (PPE, Elecricity, SWL, Danger etc.)





OK

4. Check “danger electric” marker bricks are installed at ground level and painted yellow where applicable





OK

	5.
	Rising Main acceptance testing according to standard and passed
	OK

	6.
	Gravity Main acceptance testing according to standard and passed
	OK

	7.
	‘As Constructed’ survey by licenced surveyor complete
	OK

	
	
	



8. Changes to any detail as shown on the ‘For Construction’ drawings noted on a set of ‘For Construction’ drawings and marked ‘As Constructed





OK


9. Current Unitywater Standard Drawings are on site (OR, if “Design and Construct”, the ‘For Construction’ drawings have been reviewed by Unitywater)



OK

	10.
	All required civil works testing (ITPs) completed by Contracts Inspector
	
	OK

	
	
	
	

	11.
	Operation and Maintenence Manuals have been received for Vendor supplied
	
	OK

	
	components and the Functional Specification is available
	
	

	12.
	Electical supply and metering available on site
	
	OK

	13.
	Pole / pillar termination method meets all requirements
	
	OK

	14.
	Check operation of all locks on switchboards
	
	OK

	
	
	
	



15. Check all cable supports and check for obstructions (e.g. cables not obstructing when lifting pump)





OK

	16.
	Selected control equipment is suitable for selected pump manufacturer
	OK

	17.
	Test documentation for Mechanical equipment and Instrumentation has been
	OK

	
	received. These generally include:
	



· Factory test results

· Test compliance cetificates

· Instrument calibration certificates

· Warranty information


	This document may not, in whole or part, be copied, photocopied, reproduced or translated without
	P a g e
	7

	prior consent from the CEO, Unitywater.
	
	

	
	
	


Printed copies are uncontrolled.

Document No: F8943

Revision No: 6

Last Review Date: 28/01/2021


Next Review Date: 28/01/2023

F8943 - SPS Commissioning Check Sheet Template


	18. FAT completed and critical punchlist items rectified
	
	OK

	
	
	
	

	CONSTRUCTOR
	
	
	

	
	
	
	

	Name:
	Position:
	Signature:
	Date:

	
	
	
	

	UNITYWATER SIGNOFF
	
	
	

	
	
	
	

	Name:
	Position:
	Signature:
	Date:

	
	
	
	


	This document may not, in whole or part, be copied, photocopied, reproduced or translated without
	P a g e
	8

	prior consent from the CEO, Unitywater.
	
	

	
	
	


Printed copies are uncontrolled.

Document No: F8943

Revision No: 6

Last Review Date: 28/01/2021


Next Review Date: 28/01/2023

F8943 - SPS Commissioning Check Sheet Template


PROJECT TITLE:

Pre-commissioning Checklist

General



FINANCE NO:

Result / Init. / Date

	1.
	Check Preliminaries Checklist completed and signed off
	OK

	Network
	

	
	
	

	1.
	Check Commissioning Plan has been approved by Unitywater
	OK

	
	
	



2. Advise Network Operations and Control Room of commencement of pre-commissioning acivities and proposed timing of performance and SAT testing





OK


3. Check Network Operations and Control Room are ready for performance and SAT testing and appropriate resources are availbale to assist



OK

	4.
	Confirm Network Operations are aware of impact on downstream infrastructure
	
	OK

	
	
	
	

	5.
	Advise treatment plant operators of proposed timing of performance and SAT
	
	OK

	
	testing (fluctuating load)
	
	

	6.
	Check sufficient water / recycled water is available for testing
	
	OK

	7.
	Ensure impacts on upstream infrastructure from changes to overflow level have
	
	OK

	
	been assessed
	
	

	
	
	
	


Electrical, Instruments and Control (E, I & C)


Generators

	
	1.
	Check generator mains and earth cables are installed and connected
	OK

	
	2.
	Record the cable insulation resistance of the 3 phases
	

	
	
	
	
	L1
	______ MΩ

	
	
	
	
	L2
	______ MΩ

	
	
	
	
	L3
	______ MΩ

	
	3.
	Record earth loop impedance
	______ Ω

	
	4.
	Check point-to-point phase continuity
	

	
	
	
	
	R to L1
	OK

	
	
	
	
	W to L2
	OK

	
	
	
	
	B to L3
	OK

	
	Switchboards
	

	
	
	
	

	
	5.
	ENSURE SWITCHBOARD IS NOT ENERGISED
	OK

	
	
	
	
	
	

	
	6.
	Check mains and earth cables are installed and connected
	OK

	
	
	
	
	
	


	This document may not, in whole or part, be copied, photocopied, reproduced or translated without
	P a g e
	9

	prior consent from the CEO, Unitywater.
	
	

	
	
	


Printed copies are uncontrolled.

Document No: F8943

Revision No: 6

Last Review Date: 28/01/2021


Next Review Date: 28/01/2023

F8943 - SPS Commissioning Check Sheet Template


	7.
	Record the cable insulation resistance of the 3 phases
	

	
	L1
	______ MΩ

	
	L2
	______ MΩ

	
	L3
	______ MΩ

	8.
	Record earth loop impedance
	______ Ω

	9.
	Check point-to-point phase continuity
	

	
	R to L1
	OK

	
	W to L2
	OK

	
	B to L3
	OK

	10.
	Check Incomer protection set as per design
	OK

	11.
	Check all CT and other links are in place
	OK

	12.
	Check correct glands have been utilised for cable entries
	OK

	13.
	Cable screens and earthing is as per design
	OK

	14.
	Ensure switchboard main Incomer is turned OFF and tagged
	OK

	15.
	Check MEN connection
	OK

	16.
	Turn on mains switch
	OK

	17.
	ACKNOWLEDGE SWITCHBOARD IS NOW ENERGISED
	OK

	18.
	Check 3 phase voltages
	

	
	AB
	_______ V

	
	BC
	_______ V

	
	CA
	_______ V

	Lighting and GPOs
	

	
	
	

	19.
	Check light circuit breaker conforms to electrical drawings
	OK

	20.
	GPO circuit breaker(s) conform to electrical drawings
	OK

	21.
	Check earth leakage circuit breaker has been tested and results are available
	OK

	22.
	Internal and external lights are connected and working
	OK

	23.
	Internal and external GPOs are connected and working
	OK

	
	
	


Level Transducers


24. Check surge protection barriers are installed (control panel and field). Pay particular attention to earth screen terminators.





OK


25. Check connection from hydrostatic level probe No.1 to the transmitter and confirm correct operation





OK

26. Check connection from hydrostatic level probe No.2 to the transmitter and confirm correct operation





OK


27. Check scaling conforms to wet well design requirements





OK

	This document may not, in whole or part, be copied, photocopied, reproduced or translated without
	P a g e
	10

	prior consent from the CEO, Unitywater.
	
	

	
	
	


Printed copies are uncontrolled.

Document No: F8943

Revision No: 6

Last Review Date: 28/01/2021


Next Review Date: 28/01/2023

F8943 - SPS Commissioning Check Sheet Template


Flowmeters

	28.
	Check calibration certificate has been received
	OK

	29.
	Check mag flow head is connected to flowmeter converter
	OK

	30.
	Check correct supply voltage available at converter
	OK

	31.
	Check analogue output is correctly connected to RTU and operating correctly
	OK

	32.
	Check totaliser output is correctly connected to RTU and operating correctly
	OK

	33.
	Check mechanical (vandal) and UV protection installed on external cable
	OK

	
	
	


Field Devices

	34.
	Check installation of high / overflow level switch
	OK

	35.
	Check calibration of all analogue signals (including flow and pressure transmitters)
	OK

	36.
	Check setting of pressure switches
	OK

	37.
	Verify level controller (hydrostatic probe) calibration
	OK

	
	
	


Pump Motors


38. Check pump motor name plate details have been received and applied to asset management form and electrical drawings and a second plate is mounted on the switchboard pump control door





OK

	39.
	Check pump motor name plate has been applied to MCC or disconnection box
	OK

	40.
	Record pump motor winding insulation resistance
	

	
	R-W@1000V
	______ MΩ

	
	R-B@1000V
	______ MΩ

	
	W-B@1000V
	______ MΩ

	
	R-E@1000V
	______ MΩ

	
	W-E@1000V
	______ MΩ

	
	B-E@1000V
	______ MΩ

	41.
	Record pump motor winding resistance
	

	
	U-U1
	______ Ω

	
	V–V1
	______ Ω

	
	W–W1
	______ Ω

	42.
	Check all motor protection equipment operates as specified (e.g. water in oil
	OK

	
	sensor, thermistors, vibration sensors, bearing temperatures etc.)
	

	
	
	



43. For variable frequiency drive (VFD), check drive settings are setup and settings recorded





OK


	44.
	For soft starter, confirm Soft Starter settings are setup and settings recorded
	OK

	45.
	For direct on-line (DOL) starter, check overload settings correct and recorded on
	OK

	
	drawing
	

	
	
	



46. Perform bump test to confirm correct rotation direction





OK

	This document may not, in whole or part, be copied, photocopied, reproduced or translated without
	P a g e
	11

	prior consent from the CEO, Unitywater.
	
	

	
	
	


Printed copies are uncontrolled.

Document No: F8943

Revision No: 6

Last Review Date: 28/01/2021


Next Review Date: 28/01/2023

F8943 - SPS Commissioning Check Sheet Template


47. Tag pump motor “out of service” to indicate readiness for testing





OK

Overflow and Emergency Start Circuits

	48.
	Confirm overflow level RL
	______ m RL

	49.
	Ensure overflow level switch is set up to the correct overflow level (sufficient
	OK

	
	distance below overflow to allow for switch activation) and confirm correct
	


	
	operation
	

	50.
	Check installation and correct operation of emergency start circuit
	OK

	Pump Disconnection Boxes
	

	
	
	

	51.
	Check incoming and outgoing cables have been secured correctly
	OK

	52.
	Check all conduits have been sealed to prevent gassing through conduits
	OK

	Radio
	
	

	
	
	

	53.
	Check radio feeder & antenna installation and cable testing (antenna to radio)
	OK

	
	have been performed, and results certificate received
	

	54.
	Check surge protection and fly lead is connected between antenna and radio
	OK

	55.
	Check Communications earthing kits and earthing are installed on feeder and
	OK

	
	Surge Diverter respectively
	

	
	
	

	56.
	Record radio system information
	

	
	Check & Verify Make & Model are correct
	OK

	
	Record Serial #
	_________

	57.
	Check unit is powered with correct polarity and voltage 12V DC Supply
	OK

	58.
	Check radio is programmed to the correct channel
	OK

	
	Record frequency
	______MHz

	59.
	Check radio configuration including stream id serial paramaters are set correctly
	OK

	
	for the Outstation and record
	_________

	
	
	_________

	
	
	_________

	
	
	_________

	60.
	Check data radio diagnostics communication working correctly
	OK

	Remote Telemetry Units (RTU)
	

	
	
	

	61.
	Check unit is powered with correct polarity and voltage DC Supply(ies)
	OK

	62.
	Check the UPS battery is connected and charging
	OK

	63.
	Check communication is working
	OK

	
	
	



64. Check I/O is operational and conforms with current drawings





OK

	This document may not, in whole or part, be copied, photocopied, reproduced or translated without
	P a g e
	12

	prior consent from the CEO, Unitywater.
	
	

	
	
	


Printed copies are uncontrolled.

Document No: F8943

Revision No: 6

Last Review Date: 28/01/2021


Next Review Date: 28/01/2023

F8943 - SPS Commissioning Check Sheet Template


Control System

	65.
	Record type of control system installed (i.e. SCADAPack, MultiSmart, MT2-PC)
	_________

	66.
	Record controller information
	

	
	Manufacturer
	_________

	
	Model type
	_________

	
	Serial no
	_________

	
	Firmware rev
	_________


	
	Software rev
	_________

	
	
	


End to End Testing

	67.
	Notify control room of impending end-to-end test (minimum 5 days notice)
	OK

	68.
	Check end-to-end test sheet has been reviewed and approved by control room
	OK

	69.
	Complete End-to-End Test Sheet to verify communication to SCADA
	OK

	Mechanical
	

	
	

	General
	

	
	
	

	70.
	Check layout conforms with ‘For Construction’ piping drawings
	OK

	
	
	



71. Undertake visual examination of installation and finish of all pipework, mechanical devices, valves, fittings and pump units





OK

	72.
	Check accuracy of tagging and labelling
	OK

	73.
	Check RPZD has been installed by appropriately licenced plumber
	OK

	74.
	Check functionality and accessibility of mobile crane (franna)
	OK

	
	
	



75. Check for any debris capable of causing damage to mechanical equipment when pumps are started





OK


76. Check accessibility of access covers and equipment for operational and maintenence purposes



OK

	77.
	Check equipment is guarded appropriately
	
	OK

	
	
	
	

	78.
	Check stairways, landings and access ladders comply with design requirements
	
	OK

	79.
	Check that all Device O&M Manuals are available
	
	OK

	80.
	Check that manufacturers’ requirements have been met (i.e. alignment,
	
	OK

	
	lubrication, preparation, priming etc.)
	
	

	
	
	
	



81. Check instrumentation nozzles are provided in accordance with design (correct side of equipment e.g. US/DS)





OK

	82.
	Check installation and operation of instrument isolation valves
	OK

	83.
	Check directional requirements (i.e. pump rotation, check valve direction etc.)
	OK

	
	
	



84. Check commissioning pressure transmitters or gauges on either side of pump are operational





OK

	This document may not, in whole or part, be copied, photocopied, reproduced or translated without
	P a g e
	13

	prior consent from the CEO, Unitywater.
	
	

	
	
	


Printed copies are uncontrolled.

Document No: F8943

Revision No: 6

Last Review Date: 28/01/2021


Next Review Date: 28/01/2023

F8943 - SPS Commissioning Check Sheet Template


Flowmeter

	85.
	Flowmeter calibration certificate received
	OK

	86.
	Check earthing straps are installed accross both flowmeter flanges, earthing rings
	OK

	
	and to earth as specified by the equipment manufacturer
	

	Pumps
	

	
	
	

	87.
	Check impeller has a free shaft
	OK

	88.
	Prime pumps with water
	OK

	89.
	Check correct pump curves are on site
	OK

	
	
	


Rising Main


90. Check pressure test has been undertaken according to relevant standard and passed



OK

	
	91.
	Check pipework connections to UW network have been successfully completed
	
	OK

	
	
	
	
	

	
	92.
	Charge the rising main and ensure air is purged
	
	
	OK

	
	
	
	
	
	

	
	CONSTRUCTOR
	
	
	

	
	
	
	
	
	
	

	
	Name:
	
	Position:
	Signature:
	
	Date:

	
	
	
	
	
	

	
	UNITYWATER SIGNOFF
	
	
	

	
	
	
	
	
	
	

	
	Name:
	
	Position:
	Signature:
	
	Date:

	
	
	
	
	
	
	


	This document may not, in whole or part, be copied, photocopied, reproduced or translated without
	P a g e
	14

	prior consent from the CEO, Unitywater.
	
	

	
	
	


Printed copies are uncontrolled.

Document No: F8943

Revision No: 6

Last Review Date: 28/01/2021


Next Review Date: 28/01/2023

F8943 - SPS Commissioning Check Sheet Template


Wet Testing


	PROJECT TITLE:
	FINANCE NO:


	
	Commissioning Schedule
	Result / Init. / Date
	UW Witness

	
	
	
	/ Initials

	
	
	
	

	
	General
	
	

	
	
	
	

	
	1.  Check Pre-commissioning Checklist completed and signed off
	OK
	

	
	Level Sensor Checks
	
	YES

	
	
	
	



2. Record Top of Slab RL (m) and distance from Top of Slab to each level sensor in Commissioning Worksheet




OK


3. Record well diameter and total depth for volume calculations in Commissioning Worksheet




OK


4. Confirm wet well level indicated by the level probe is reflective of the actual wet well level and record readings in Commissioning Worksheet




OK


5. Confirm functioning of high and high high (overflow) level alarms

Note that the overflow structure may only be brought on-line once ‘As Constructed’ overflow level has been confirmed (to remain bunged off until level confirmed)





OK

Pump Checks


Motor Checks



YES


	6.
	Ensure correct parameters are set in the VFD or Soft Starter if applicable
	OK
	

	
	
	
	

	7.
	Start pump with discharge valve closed and ensure the pump is running
	OK
	

	
	without undue noise, vibration and temperature
	
	

	8.
	To ensure motor load balancing, record:
	
	

	
	Pump running amps L1
	________A
	

	
	Pump running amps L2
	________A
	

	
	Pump running amps L3
	________A
	

	9.
	Stop pump
	OK
	

	10.
	Complete Low Power Tuning (Danfoss VFD) and record values into
	OK
	

	
	Commissioning Worksheet
	
	

	11.
	Repeat steps 7 to 10 for second pump/drive
	OK
	

	Fill and Bleed Rising Main
	
	YES

	
	
	
	

	12.
	Calculate volume of water required to fill rising main
	OK
	

	
	
	
	



13. Ensure sufficient water in wet well to fill rising main and perform pump operation test





OK

	This document may not, in whole or part, be copied, photocopied, reproduced or translated without
	P a g e
	15

	prior consent from the CEO, Unitywater.
	
	

	
	
	


Printed copies are uncontrolled.

Document No: F8943

Revision No: 6

Last Review Date: 28/01/2021


Next Review Date: 28/01/2023

F8943 - SPS Commissioning Check Sheet Template


	14.
	Open pump discharge valve
	OK
	

	15.
	Run pump and bleed air from rising main
	OK
	

	16.
	Operate pump from 35 to 50 Hz in 5 Hz increments (if VFD type), check for
	OK
	

	
	abnormal movement or vibration
	
	

	17.
	Perform visual inspection of pump, all piping, fittings and flanged joints for
	OK
	

	
	leakage
	
	

	
	
	
	



Pump Performance and Flowmeter Accuracy





YES

	18.
	Complete Draw Down test and verify flowmeter accuracy
	

	
	
	OK
	

	19.
	Complete Pump Performance test including shutoff head
	OK
	

	20.
	Use Commissioning Worksheet to record and assess results
	OK
	

	
	
	
	


Pump Control Checks


Duty Pump Fault Test (2 pumps)



YES


	
	
	21.
	Select both pumps to “off” position
	OK
	
	

	
	
	
	
	
	
	

	
	
	22.
	Ensure assist start level > wet well level > duty start level
	OK
	
	

	
	
	23.
	Ensure pump discharge valves are open
	OK
	
	

	
	
	24.
	Confirm both drives have no faults present
	OK
	
	

	
	
	25.
	Select Pump 1 (Duty Pump) to “automatic” position
	OK
	
	

	
	
	26.
	Confirm Duty Pump running
	OK
	
	

	
	
	27.
	Select Pump 2 (Duty Assist) to “automatic” position
	OK
	
	

	
	
	28.
	Fault Duty Pump – i.e. open one c/b feeder for phase failure relay
	OK
	
	

	
	
	29.
	Confirm Duty Assist pump starts
	OK
	
	

	
	
	30.
	Stop system – both pumps to “off” position
	OK
	
	

	
	
	31.
	Select Pump 2 as Duty Pump
	OK
	
	

	
	
	32.
	Select Pump 1 as Duty Assist
	OK
	
	

	
	
	33.
	Repeat Steps 22 to 30
	OK
	
	

	
	
	Duty / Assist Test (2 pumps)
	
	YES

	
	
	
	
	
	
	

	
	
	34.
	Select both pumps to “off” position
	OK
	
	

	
	
	35.
	Ensure assist start level > wet well level > duty start level
	OK
	
	

	
	
	36.
	Ensure pump discharge valves are open
	OK
	
	

	
	
	37.
	Confirm both drives have no faults present
	OK
	
	

	
	
	38.
	Select both pumps to “automatic” position
	OK
	
	

	
	
	39.
	Confirm Pump 2 (Duty Pump) running
	OK
	
	

	
	
	
	
	
	
	

	This document may not, in whole or part, be copied, photocopied, reproduced or translated without
	P a g e
	16

	prior consent from the CEO, Unitywater.
	
	

	
	
	


Printed copies are uncontrolled.

Document No: F8943

Revision No: 6

Last Review Date: 28/01/2021


Next Review Date: 28/01/2023

F8943 - SPS Commissioning Check Sheet Template


	40.
	Manually override wet well level > than assist start level
	OK
	

	41.
	Confirm Assist Pump started
	OK
	

	42.
	Manually override wet well level < assist stop level
	OK
	

	43.
	Confirm Duty Assist stopped
	OK
	

	44.
	Manually override wet well level < duty stop level
	OK
	

	45.
	Confirm Duty Pump stopped
	OK
	

	46.
	Select Pump 1 as Duty Pump
	OK
	

	47.
	Select Pump 2 as Duty Assist
	OK
	

	48.
	Repeat Steps 35 to 45
	OK
	

	49.
	Select both pumps to “off” position
	OK
	

	Pump Cycling
	
	YES

	
	
	
	

	50.
	Manually override wet well level < duty stop level (pumps are stopped)
	OK
	

	51.
	Ensure wet well level > duty start level
	OK
	

	52.
	Confirm both drives have no faults present
	OK
	

	53.
	Ensure pump discharge valves are open
	OK
	

	54.
	Select both pumps to “automatic” position
	OK
	

	55.
	Record which pump is selected as Duty Pump by controller
	______
	

	56.
	Manually override wet well level > duty start level
	OK
	

	57.
	Confirm Duty Pump running
	OK
	

	58.
	Manually override wet well level < duty stop level
	OK
	

	59.
	Confirm Duty Pump stopped
	OK
	

	60.
	Record which pump is selected as Duty Pump by controller
	______
	

	61.
	Select both pumps to “off” position
	OK
	

	Emergency Start Circuit
	
	YES

	
	
	
	

	62.
	Ensure sufficient water in wet well for test
	OK
	

	63.
	Turn off the RTU
	OK
	

	64.
	Select both pumps to “automatic” position
	OK
	

	65.
	Simulate a wet well high high level (manually lowering the probe is the
	OK
	

	
	preferred method)
	
	

	66.
	Confirm Pump 1 starts
	OK
	

	67.
	Confirm Pump 2 starts (after pump 2 start delay)
	OK
	

	
	
	
	



68. Confirm both pumps stop when water level reaches the lowest probe (stop) on the start/stop three point probe





OK

	This document may not, in whole or part, be copied, photocopied, reproduced or translated without
	P a g e
	17

	prior consent from the CEO, Unitywater.
	
	

	
	
	


Printed copies are uncontrolled.

Document No: F8943

Revision No: 6

Last Review Date: 28/01/2021


Next Review Date: 28/01/2023

F8943 - SPS Commissioning Check Sheet Template


	69.
	Select both pumps to “off” position
	OK
	

	70.
	Turn on the RTU
	OK
	

	Generator Checks
	
	YES

	
	
	
	

	71.
	Ensure sufficient water in wet well for test
	OK
	

	72.
	Ensure generator main switch is off
	OK
	

	73.
	Select both pumps to “off” position
	OK
	

	74.
	Connect generator and check all connections
	OK
	

	75.
	Start generator and check phase direction and voltages
	OK
	

	76.
	Select changeover switch to generator supply
	OK
	

	77.
	Close main switch and check all voltages
	OK
	

	78.
	Select Pump 1 to “automatic” and confirm correct operation
	OK
	

	
	NOTE: If sufficient water available for testing allow system to cycle confirming
	
	

	
	complete functionality. Otherwise override wet well level to confirm pump
	
	

	
	operation.
	
	

	
	
	
	



79. Select Pump 2 to “automatic” and confirm correct operation

Note due to portable generator size potentially both pumps may not be able to run and shall be decided on an individual site basis.





OK

	
	80.
	Select both pumps to “off” position
	OK
	

	
	81.
	Restore mains power and disconnect generator
	OK
	

	
	
	
	
	


Wet Testing Signoff

CONSTRUCTOR

Name:



Position:



Signature:



Date:

UNITYWATER WITNESS


Name:

Name:

Name:



	Position:
	Signature:
	Date:

	Position:
	Signature:
	Date:

	Position:
	Signature:
	Date:

	
	
	



	This document may not, in whole or part, be copied, photocopied, reproduced or translated without
	P a g e
	18

	prior consent from the CEO, Unitywater.
	
	

	
	
	


Printed copies are uncontrolled.

Document No: F8943

Revision No: 6

Last Review Date: 28/01/2021


Next Review Date: 28/01/2023

F8943 - SPS Commissioning Check Sheet Template


SAT / Performance Testing


PROJECT TITLE:

SAT Schedule

SAT Pre-start Checks



FINANCE NO:


Result / Init. / Date

	1.
	Check Wet Testing Checklist completed and signed off
	OK

	2.
	Check SAT attendees are inducted to site
	OK

	
	
	


Level Sensor Checks


3. Record Top of Slab RL (m) and distance from Top of Slab to each level sensor in Commissioning Worksheet




OK


4. Record well diameter and total depth for volume calculations in Commissioning Worksheet




OK


5. Confirm wet well level indicated by the level probe is reflective of the actual wet well level and record readings in Commissioning Worksheet




OK


6. Confirm functioning of high and high high (overflow) level alarms

Note that the overflow structure may only be brought on-line once ‘As Constructed’ overflow level has been confirmed (to remain bunged off until level confirmed)





OK

Pump Checks


Pump Performance and Flowmeter Accuracy

	7.
	Complete Draw Down test and verify flowmeter accuracy
	OK

	8.
	Complete Pump Performance test including shutoff head
	OK

	9.
	Transfer readings into Commissioning Worksheet and assess results
	OK

	
	
	


Pump Control Checks


Duty Pump Fault Test (2 pumps)

	
	10.
	Select both pumps to “off” position
	OK

	
	11.
	Ensure assist start level > wet well level > duty start level
	OK

	
	12.
	Ensure pump discharge valves are open
	OK

	
	13.
	Confirm both drives have no faults present
	OK

	
	14.
	Select Pump 1 (Duty Pump) to “automatic” position
	OK

	
	15.
	Confirm Duty Pump running
	OK

	
	
	
	


	This document may not, in whole or part, be copied, photocopied, reproduced or translated without
	P a g e
	19

	prior consent from the CEO, Unitywater.
	
	

	
	
	


Printed copies are uncontrolled.

Document No: F8943

Revision No: 6

Last Review Date: 28/01/2021


Next Review Date: 28/01/2023

F8943 - SPS Commissioning Check Sheet Template


	16.
	Select Pump 2 (Duty Assist) to “automatic” position
	OK

	17.
	Fault Duty Pump – i.e. open one c/b feeder for phase failure relay
	OK

	18.
	Confirm Duty Assist pump starts
	OK

	19.
	Stop system – both pumps to “off” position
	OK

	20.
	Select Pump 2 as Duty Pump
	OK

	21.
	Select Pump 1 as Duty Assist
	OK

	22.
	Repeat Steps 11 to 19
	OK

	Duty / Assist Test (2 pumps)
	

	
	
	

	23.
	Select both pumps to “off” position
	OK

	24.
	Ensure assist start level > wet well level > duty start level
	OK

	25.
	Ensure pump discharge valves are open
	OK

	26.
	Confirm both drives have no faults present
	OK

	27.
	Select both pumps to “automatic” position
	OK

	28.
	Confirm Pump 2 (Duty Pump) running
	OK

	29.
	Manually override wet well level > than assist start level
	OK

	30.
	Confirm Assist Pump started
	OK

	31.
	Manually override wet well level < assist stop level
	OK

	32.
	Confirm Duty Assist stopped
	OK

	33.
	Manually override wet well level < duty stop level
	OK

	34.
	Confirm Duty Pump stopped
	OK

	35.
	Select Pump 1 as Duty Pump
	OK

	36.
	Select Pump 2 as Duty Assist
	OK

	37.
	Repeat Steps 24 and 34
	OK

	38.
	Select both pumps to “off” position
	OK

	Pump Cycling
	

	
	
	

	39.
	Manually override wet well level < duty stop level (pumps are stopped)
	OK

	40.
	Ensure wet well level > duty start level
	OK

	41.
	Confirm both drives have no faults present
	OK

	42.
	Ensure pump discharge valves are open
	OK

	43.
	Select both pumps to “automatic” position
	OK

	44.
	Record which pump is selected as Duty Pump by controller
	_________

	45.
	Manually override wet well level > duty start level
	OK

	
	
	


	This document may not, in whole or part, be copied, photocopied, reproduced or translated without
	P a g e
	20

	prior consent from the CEO, Unitywater.
	
	

	
	
	


Printed copies are uncontrolled.

Document No: F8943

Revision No: 6

Last Review Date: 28/01/2021


Next Review Date: 28/01/2023

F8943 - SPS Commissioning Check Sheet Template


	46.
	Confirm Duty Pump running
	OK

	47.
	Manually override wet well level < duty stop level
	OK

	48.
	Confirm Duty Pump stopped
	OK

	49.
	Record which pump is selected as Duty Pump by controller
	_________

	50.
	Select both pumps to “off” position
	OK

	Emergency Start Circuit
	

	
	
	

	51.
	Ensure sufficient water in wet well for test
	OK

	52.
	Turn off the RTU
	OK

	53.
	Select both pumps to “automatic” position
	OK

	54.
	Simulate a wet well high high level (manually lowering the probe is the preferred
	OK

	
	method)
	

	55.
	Confirm Pump 1 starts
	OK

	56.
	Wait for several seconds (Pump 2 start delay)
	OK

	57.
	Confirm Pump 2 starts
	OK

	
	
	



58. Confirm both pumps stop when water level reaches the lowest probe (stop) on the start/stop three point probe





OK


59. Select both pumps to “off” position

60. Turn on the RTU





OK


OK

Generator Checks

	61.
	Ensure sufficient water in wet well for test
	OK

	62.
	Ensure generator main switch is off
	OK

	63.
	Select both pumps to “off” position
	OK

	64.
	Connect generator and check all connections
	OK

	65.
	Start generator and check phase direction and voltages
	OK

	66.
	Select changeover switch to generator supply
	OK

	67.
	Close main switch and check all voltages
	OK

	68.
	Select Pump 1 to “automatic” and confirm correct operation
	OK

	
	NOTE: If sufficient water available for testing allow system to cycle confirming
	

	
	complete functionality. Otherwise override wet well level to confirm pump
	

	
	operation.
	

	
	
	



69. Select Pump 2 to “automatic” and confirm correct operation

Note due to portable generator size potentially both pumps may not be able to run and shall be decided on an individual site basis



OK

	
	
	70.
	Select both pumps to “off” position
	
	OK

	
	
	
	
	
	

	
	
	71.
	Restore mains power and disconnect generator
	
	OK

	
	
	
	
	
	

	This document may not, in whole or part, be copied, photocopied, reproduced or translated without
	P a g e
	21

	prior consent from the CEO, Unitywater.
	
	

	
	
	


Printed copies are uncontrolled.

Document No: F8943

Revision No: 6

Last Review Date: 28/01/2021


Next Review Date: 28/01/2023

F8943 - SPS Commissioning Check Sheet Template


SAT Signoff

To verify completion of all SAT items to the satisfaction of Stakeholders.

CONSTRUCTOR

Name:



Position:



Signature:



Date:

UNITYWATER WITNESS (Commissioning)

Name:



Position:



Signature:



Date:

UNITYWATER WITNESS (Operations)

Name:



Position:



Signature:



Date:

UNITYWATER WITNESS (Electrical)

Name:



Position:



Signature:



Date:

UNITYWATER WITNESS (SCADA)

Name:



Position:



Signature:



Date:

UNITYWATER WITNESS (Mechanical)


Name:



Position:



Signature:





Date:

	This document may not, in whole or part, be copied, photocopied, reproduced or translated without
	P a g e
	22

	prior consent from the CEO, Unitywater.
	
	

	
	
	


Printed copies are uncontrolled.

